**  Elevator Sprinkler Requirements **

If sprinkler heads are installed in the elevator shaft or machine room, the elevator code requires a means be provided to automatically disconnect the main line power supply to the affected elevator, upon or prior to the application of water from the sprinkler.

This is commonly accomplished by installing a Shunt Trip Breaker in line with the main line power for the elevator.  Heat sensors are then installed within two (2) feet of each sprinkler head.  The heat sensors are wired so as to trip the shunt trip breaker when a predetermined heat is reached.  The activating heat of the head sensor should be lower than the activating heat for the sprinkler head.

If you have any questions or require additional information please call Jersey Elevator Company at (800) 621-0145.