**  Elevator Smoke Detector Requirements **

The elevator code requires certain smoke detectors initiate a fire recall operation of the elevator.  In order to accomplish this, Jersey Elevator Company, Inc. requires the following:

1)   Smoke detectors installed in each elevator lobby, the

top of the elevator shaft, and in the elevator machine

room.

2)   Four (4) relay modules installed near the elevator

control board – each equipped with normally open and

closed contacts rated to handle 110VAC, 1 amp.

3)   Relay modules should energize as follows:

Module 1 – When the main floor lobby smoke is

activated.

Module 2 -  When any lobby smoke other than the main

floor smoke is activated.

Module 3 -  When the machine room smoke is activated.

Module 4 -  When the top of shaft smoke is activated.

NOTE:  If a smoke detector is installed in the elevator pit, please call

Jersey Elevator.

If you have any questions or require additional information please call Jersey Elevator Company Inc. at (800) 621-0145.